## 读数据 Read data
读数据Read data
功能名称 Feature name | 控制码（1个字节） Control code (1 byte) | 数据长度（字节） Data length (bytes) | 标识码 Identification code | 数据格式 Data format | 举例 For example | 解析 Parse | 单位 Unit
有功总电量 Active total power | 0x11 | 4 | 0x00000000 | XXXXXX.XX(BCD) | 12 34 56 78 | 785634.12 | Kwh
有功费率1 Active Tariff 1 | 0x11 | 4 | 0x00000100 | XXXXXX.XX(BCD) | 12 34 56 78 | 785634.12 | Kwh
有功费率2 Active Tariff 2 | 0x11 | 4 | 0x00000200 | XXXXXX.XX(BCD) | 12 34 56 78 | 785634.12 | Kwh
有功费率3 Active Tariff 3 | 0x11 | 4 | 0x00000300 | XXXXXX.XX(BCD) | 12 34 56 78 | 785634.12 | Kwh
有功费率4 Active Tariff 4 | 0x11 | 4 | 0x00000400 | XXXXXX.XX(BCD) | 12 34 56 78 | 785634.12 | Kwh
有功电量数据块 Active energy data block | 0x11 | 4*5 | 0x0000FF00 | XXXXXX.XX(BCD) | 同上，顺序为总、1234 Same as above, in the order of total, 1234 | / | Kwh
电压 Voltage | 0x11 | 2 | 0x02010100 | XXX.X(BCD) | 12 34 | 341.2 | V
电流 Current | 0x11 | 3 | 0x02020100 | XXX.XXX(BCD) | 12 34 56 | 563.412 | A
日期及星期 Date and week | 0x11 | 4 | 0x04000101 | YYMMDDWW(BCD) | 02 21 04 19 | 19-04-21星期二 19-04-21 Tuesday | /
时间 Time | 0x11 | 3 | 0x04000102 | hhmmss(BCD) | 45 23 12 | 12:23:45 | /
轮显时间 Scroll display time | 0x11 | 1 | 0x04000302 | XX(BCD) | 34 | 34 | 秒 Second
序列号 Serial No. | 0x11 | 6 | 0x04000401 | XXXXXXXXXXXX(BCD) | 23 43 67 89 54 27 | 275489674323 | /
时段表 Time interval sheet | 0x11 | 3*8 | 0x04010001 | HHMMRR*8(BCD) | 02 45 21 | 21:45费率2 21:45 Tariff 2 | /
软件版本号 Software version No. | 0x11 | 32 | 0x04800001 | ASCII | / | / | /
硬件版本号 Hardware version No. | 0x11 | 32 | 0x04800002 | ASCII | / | / | /
过压事件记录 Overvoltage event record | 0x11 | 12 | 0x50000400-0x50000413 | YYMMDDhhmmssYYMMDDhhmmss | 34 22 13 12 01 19 32 35 13 12 01 19 | 事件开始:19-01-12 13:22:34 事件恢复:19-01-12 13:35:32 Event start: 19-01-12 13:22:34 Event resumed: 19-01-12 13:35:32 | /
过压阈值+过压触发时间 Overvoltage threshold + overvoltage trigger time | 0x11 | 2+1 | 0x50000420 | XXXX(BCD)+XX(BCD) | 34 02 12 | 234V+12s | /
欠压事件记录 Undervoltage event record | 0x11 | 12 | 0x50000500-0x50000513 | YYMMDDhhmmssYYMMDDhhmmss | 34 22 13 12 01 19 32 35 13 12 01 19 | 事件开始:19-01-12 13:22:34 事件恢复:19-01-12 13:35:32 Event start: 19-01-12 13:22:34 Event resumed: 19-01-12 13:35:32 | /
欠压阈值+欠压触发时间 Undervoltage threshold + undervoltage trigger time | 0x11 | 2+1 | 0x50000520 | XXXX(BCD)+XX(BCD) | 34 02 12 | 234V+12s | /
过流事件记录 Overcurrent event record | 0x11 | 12 | 0x50000600-0x50000613 | YYMMDDhhmmssYYMMDDhhmmss | 34 22 13 12 01 19 32 35 13 12 01 19 | 事件开始:19-01-12 13:22:34 事件恢复:19-01-12 13:35:32 Event start: 19-01-12 13:22:34 Event resumed: 19-01-12 13:35:32 | /
过流阈值+过流触发时间 Overcurrent threshold + overcurrent trigger time | 0x11 | 2+1 | 0x50000620 | XXXX(BCD)+XX(BCD) | 34 02 12 | 234A+12s | /
阈值统一读取 Threshold uniform read | 0x11 | 9 | 0x50000640 | XXXX(BCD) | 顺序为过压、欠压、过流 The sequence is overvoltage, undervoltage, overcurrent | / | /
停电事件记录 Power outage event record | 0x11 | 12 | 0x50000700-0x50000713 | YYMMDDhhmmssYYMMDDhhmmss | 34 22 13 12 01 19 32 35 13 12 01 19 | 事件开始:19-01-12 13:22:34 事件恢复:19-01-12 13:35:32 Event start: 19-01-12 13:22:34 Event resumed: 19-01-12 13:35:32 | / | PS:D613001不支持 D613001 not supported

## 写数据 Write data
写数据Write data
功能名称 Feature name | 控制码（1个字节） Control code (1 byte) | 数据长度（字节） Data length (bytes) | 标识码 Identification code | 数据格式 Data Format | 举例 For example | 解析 Parse | 单位 Unit
日期及星期 Date and week | 0x14 | 4 | 0x04000101 | YYMMDDWW(BCD) | 02 21 04 19 | 19-04-21星期二 19-04-21 Tuesday | /
时间 Time | 0x14 | 3 | 0x04000102 | hhmmss(BCD) | 45 23 12 | 12:23:45 | /
轮显时间 Scroll display time | 0x14 | 1 | 0x04000302 | XX(BCD) | 34 | 34 | 秒 Second
序列号 Serial No. | 0x14 | 6 | 0x04000401 | XXXXXXXXXXXX(BCD) | 23 43 67 89 54 27 | 275489674323 | /
时段表 Time interval sheet | 0x14 | 3*8 | 0x04010001 | HHMMRR*8(BCD) | 02 45 21 | 21:45费率2 21:45 tariff 2 | /
置起升级标志 Set up the upgrade flag | 0x14 | 5 | 0x50000001 | ASCII | 4A 53 4C 54 59 | YTLSJ | /
过压阈值+触发时间 Overvoltage threshold + trigger Time | 0x14 | 2+1 | 0x50000420 | XXXX(BCD)+XX(BCD) | 34 02 12 | 234V+12s | /
欠压阈值+触发时间 Undervoltage threshold + trigger time | 0x14 | 2+1 | 0x50000520 | XXXX(BCD)+XX(BCD) | 34 02 12 | 234V+12s | /
过流阈值+触发时间 Overcurrent threshold + trigger time | 0x14 | 2+1 | 0x50000620 | XXXX(BCD)+XX(BCD) | 34 02 12 | 234A+12A | /
阈值统一设置 Threshold uniform setting | 0x14 | 9 | 0x50000640 | XXXX(BCD)+XX(BCD) | 顺序为过压、欠压、过流 The sequence is overvoltage, undervoltage, overcurrent | / | /

## 其他 Other
其他Other
DLT645-2007其他控制符支持 DLT645-2007 other control characters support | 控制符 Control character
读通讯地址 Read the communication address | 0x13
写通讯地址 Write the communication address | 0x15
改密码 Change password | 0x18
电量清零 Power reset | 0x1A
事件清零 Event clear | 0x1B